## Preamble-Indian
DOCUMENT NO. PA - I
Tender no.: 05/51/23VC/IGGL/071 ITEM :UPS SYSTEM FOR PIPELINE SECTIONS (1,2,3,4,5,6,7,8,9,12,13&14) UNDER NORTH EAST GAS GRID PIPELINE PROJET OF M/s IGGL
PREAMBLE TO UNPRICE SCHEDULE
1 | Scope of Supply including testing, Inspection, documentation etc., shall be strictly as per Material Requisition and Bidding Document.
2 | Bidder to clearly indicate 'Quoted' against each Sr. No. in the price column in the unpriced Price Schedule and % of taxes duties against relevant columns of taxes and duties. Bidders to submit Price part of above Price schedule in their Priced Bid and Unpriced part with the Unpriced Bid.
3 | Bidder shall furnish prices/details as above, in accordance with ITB .
4 | All the Columns of quoted items in the price schedule including currency must be filled with required information, as applicable.
5 | Bidder must quote the price in enclosed Price Schedule formats only. The formats shall not be changed and/or retyped. For any deviation to the formats, offer may be rejected.
6 | Quoted prices are firm and fixed till complete execution of the entire order.
7 | VOID
8 | In case of discrepancy between unit price and the total price, the unit price shall prevail. If there is a discrepancy between the total amount and the sum of total price, the sum of total price shall prevail.
9 | Bidder confirm that contents of the preamble to the price schedule, bid document, material requisition and quoted his prices accordingly without any deviation.
BIDDER'S SIGNATURE:
COMPANY'S NAME:
SEAL:
Notes: | Bidders (India) must submit this preamble with document no. PA-1 with both unpriced & priced offer.

## PS-UPS Supply
UNPRICE SCHEDULE FOR SUPPLY COMPONENT
UPS SYSTEM FOR PIPELINE SECTIONS (1,2,3,4,5,6,7,8,9,12,13&14) UNDER NORTH EAST GAS GRID PIPELINE PROJET OF M/s IGGL Tender no.: 05/51/23VC/IGGL/071
BIDDER: M/S __________________________
Item Sl. No. as per MR | Description of Items as per MR | Unit | Qty (Nos.) | Ex-works price (including packing, forwarding, and GST on components and raw materials but excluding Inland Transportation to Delivery Location) including cost of Inspection by Third Party Agency, mandatory spares etc. (wherever applicable) | Inland transportation upto Delivery location and other costs incidental to delivery of goods | GST (CGST&SGST/UTGST or IGST) on the finished goods excluding inland transportation (i.e. on cl. no. 4 ) |  | GST (CGST&SGST/UTGST or IGST) on inland transportation (i.e. on cl. no. 5) |  | Unit FOT site price incl. inland transportaion, GST etc. |  | Total FOT site price incl. inland transportaion, GST etc. |  | Harmonized System Nomenclature (HSN)
[6 empty] | % | Amount | % | Amount | In Figure | In Words | In Figure | In Words
1 | 2.a | 2.b | 3 | (4) | (5) | (6) |  | (7) |  | (8)= (4)+(5)+(6)+ (7) |  | (9)= (8) X (3) |  | (10)
1 | ITEM#1- 25KVA UPS SYSTEM
SUPPLY OF UPS SYSTEM IN ASSAM STATE (REFER SCOPE OF WORK/MR FOR LOCATION OF THE SYSTEM)
Design, Detailed Engineering, Manufacturing, Inspection/FAT (Factory acceptance test), Supply, Transportation, loading/unloading, insurance, Storage at warehouse/store in covered area (hired by bidder) of complete UPS system alongwith battery set mentioned below & as per tender specification, data sheet enclosed including commissioning spares as required at terminals :
1.1 | 25KVA, 230 V Single phase, 50 Hz, parallel redundant industrial type, UPS system suitable for input Power supply voltage of 320 V-460V- TPN (184-265V/Ph), output 230 V +/- 1%, AC with solid state voltage stabilizer for Bypass supply, ACDB and 12.0 hrs. Battery backup (Ni-Cd, 1.2V) and battery capacity shall not be less than 465 KVAh (where KVAH = battery AH x 1.2 V x No. of cells). Charger rating Shall not be Less than 140 KW. Supply & Handover of 2 year O&M spares as per list attached in scope of work, is also in the scope of supplier. | Nos. | 3
1.2 | Dual redundant Rectifier system (AC ro DC) and DCDB as per specification and following rating : (i) 48 V DCDB (3000 W) (ii)24 V DCDB (4000 W) | Nos. | 3
1.3 | All interconnecting cables among UPS, Rectifier, battery stand, ACDB/DCDB etc (50 mtr shall be considered between battery bank and UPS panel, 50 mtr each cable shall be considered between ACDB & DCDB to UPS panel) | Set | 3
2 | ITEM#2- 10KVA UPS SYSTEM
SUPPLY OF UPS SYSTEM IN ASSAM/ ARUNACHAL PRADESH/ TRIPURA/MEGHALAYA STATE/MIZORAM/NAGALAND (REFER SCOPE OF WORK/MR FOR LOCATION OF THE SYSTEM)
Design, Detailed Engineering, Manufacturing, Inspection/FAT (Factory acceptance test), Supply, Transportation, loading/unloading, insurance, Storage at warehouse/store in covered area (hired by bidder) of complete UPS system alongwith battery set mentioned below & as per tender specification, data sheet enclosed including commissioning spares as required at terminals :
2.1 | 10KVA, 230 V Single phase, 50 Hz, parallel redundant industrial type, UPS system suitable for input Power supply voltage of 320 V-460V- TPN (184-265V/Ph), output 230 V +/- 1%, AC with solid state voltage stabilizer for Bypass supply, ACDB and 12.0 hrs. Battery backup (Ni-Cd, 1.2V) and battery capacity shall not be less than 186 KVAh (where KVAH = battery AH x 1.2 V x No. of cells). Charger rating Shall not be Less than 54 KW. Supply & Handover of 2 year O&M spares as per list attached in scope of work, is also in the scope of supplier. | Nos. | 5
2.2 | Dual redundant Rectifier system (AC ro DC) and DCDB as per specification and following rating : (i) 48 V DCDB (2500 W) (ii)24 V DCDB (3500 W) | Nos. | 5
2.3 | All interconnecting cables among UPS, Rectifier, battery stand, ACDB/DCDB etc (50 mtr shall be considered between battery bank and UPS panel, 50 mtr each cable shall be considered between ACDB & DCDB to UPS panel) | Set | 5
3 | ITEM#3- 5KVA UPS SYSTEM
SUPPLY OF UPS SYSTEM IN ASSAM/ ARUNACHAL PRADESH/ TRIPURA/MEGHALAYA STATE/MIZORAM/NAGALAND (REFER SCOPE OF WORK/MR FOR LOCATION OF THE SYSTEM)
Design, Detailed Engineering, Manufacturing, Inspection/FAT (Factory acceptance test), Supply, Transportation, loading/unloading, insurance, Storage at warehouse/store in covered area (hired by bidder) of complete UPS system alongwith battery set mentioned below & as per tender specification, data sheet enclosed including commissioning spares as required at terminals :
3.1 | 5KVA, 230 V Single phase, 50 Hz, parallel redundant industrial type, UPS system suitable for input Power supply voltage of 320 V-460V- TPN (184-265V/Ph), output 230 V +/- 1%, AC with solid state voltage stabilizer for Bypass supply, ACDB and 12.0 hrs. Battery backup (Ni-Cd, 1.2V) and battery capacity shall not be less than 93 KVAh (where KVAH = battery AH x 1.2 V x No. of cells). Charger rating Shall not be Less than 27 KW. Supply & Handover of 2 year O&M spares as per list attached in scope of work, is also in the scope of supplier. | Nos. | 13
3.2 | Dual redundant Rectifier system (AC to DC) and DCDB as per specification and following rating : (i) 48 V DCDB (2000 W) (ii) 24 V DCDB (2500W) | Nos. | 13
3.3 | All interconnecting cables among UPS, Rectifier, battery stand, ACDB/DCDB etc (50 mtr shall be considered between battery bank and UPS panel, 50 mtr each cable shall be considered between ACDB & DCDB to UPS panel) | Set | 13
Total price including all costs, freight, insurance till commissioning, GST etc.
| NOTE: 1.0 The above shall be read in conjunction with notes of MR enclosed with Vol II of II. 2.0 For Statewise quantity breakup please refer scope of work. | [8 empty] | BIDDER'S SIGNATURE:
COMPANY'S NAME:
SEAL:
IGGL
MECON LIMITED

## UPS Site work
UNPRICE SCHEDULE FOR SITE WORKS
UPS SYSTEM FOR PIPELINE SECTIONS (1,2,3,4,5,6,7,8,9,12,13&14) UNDER NORTH EAST GAS GRID PIPELINE PROJET OF M/s IGGL Tender no.: 05/51/23VC/IGGL/071
BIDDER: M/S __________________________
Sl. No. | Description as per MR | Unit | Qty | Unit Price inclusive of all cost, levies etc. but excluding GST (CGST&SGST/UTGST or IGST) | GST (CGST&SGST/UTGST or IGST applicable on Col. (5) |  | Unit Price inclusive of all cost, levies etc. including GST (CGST&SGST/UTGST or IGST) |  | Total Price inclusive of all cost, levies etc. including GST (CGST&SGST/UTGST or IGST) |  | Service Accounting Codes (SAC)
[5 empty] | % | Amount | In Figure | In Words | In Figure | In Words
1 | 2 | 3 | 4 | 5 | 6 |  | 7 = 5+6 |  | 8 = 4 x 7 |  | 9
1 | ITEM#1- 25KVA UPS SYSTEM
INSTALLATION, TESTING & COMMISSIONING OF UPS SYSTEM IN ASSAM STATE
Loading/unloading, transportation from warehouse/store (hired by bidder) to site, fabrication, assembly, all mechanical works for installation, erection, commissioning and performance test at site of complete UPS system alongwith bettery sets as mentioned below & as per tender specification, data sheet, PJS enclosed including commissioning spares as required at terminals. The scope also includes submission of first trial/commissioning reports of each location, submission of engineering drawings & documents for approval from IGGL / MECON for UPS System Installation, all other work not indicated here but required for completion of installation & commissioning as per the scope of work in the scope of bidder. Work shall be crried out as per relevant international & national standard, scope of work & specifications, approved drawings & documents.
1.1 | 25KVA, 230 V Single phase, 50 Hz, parallel redundant industrial type, UPS system suitable for input Power supply voltage of 320 V-460V- TPN (184-265V/Ph), output 230 V +/- 1%, AC with solid state voltage stabilizer for Bypass supply, ACDB and 12.0 hrs. Battery backup (Ni-Cd, 1.2V) and battery capacity shall not be less than 465 KVAh (where KVAH = battery AH x 1.2 V x No. of cells). Charger rating Shall not be Less than 140 KW. | Nos. | 3
1.2 | Dual redundant Rectifier system (AC ro DC) and DCDB as per specification and following rating : (i) 48 V DCDB (3000 W) (ii)24 V DCDB (4000 W) | Nos. | 3
1.3 | All interconnecting cables among UPS, Rectifier, battery stand, ACDB/DCDB etc (50 mtr shall be considered between battery bank and UPS panel, 50 mtr each cable shall be considered between ACDB & DCDB to UPS panel) | Set | 3
1.4 | All inclusive per month rates for maintaining the warehouse/store at site (for supplied material) during the extended period as required (payable if site is not ready even after 6 months of Contractual completion date of Supply, Installation, Testing & commissioning as per terms & condition of contract and as defined in the tender scope of work). | Months | 12
1.5 | 5 years comprehensive AMC for all UPS Supplied. However AMC of these UPS shall start after successful completion of warranty period/ Defect Liability period as per contract. (For detail scope & payment terms refer scope of work & contract document) | LS | 1
2 | ITEM#2- 10KVA UPS SYSTEM
INSTALLATION, TESTING & COMMISSIONING OF UPS SYSTEM IN ASSAM/ ARUNACHAL PRADESH/ TRIPURA/MEGHALAYA STATE/MIZORAM/NAGALAND (REFER SCOPE OF WORK/MR FOR LOCATION OF THE SYSTEM)
Loading/unloading, transportation from warehouse/store (hired by bidder) to site, fabrication, assembly, all mechanical works for installation, erection, commissioning and performance test at site of complete UPS system alongwith bettery sets as mentioned below & as per tender specification, data sheet, PJS enclosed including commissioning spares as required at terminals. The scope also includes submission of first trial/commissioning reports of each location, submission of engineering drawings & documents for approval from IGGL / MECON for UPS System Installation, all other work not indicated here but required for completion of installation & commissioning as per the scope of work in the scope of bidder. Work shall be crried out as per relevant international & national standard, scope of work & specifications, approved drawings & documents.
2.1 | 10KVA, 230 V Single phase, 50 Hz, parallel redundant industrial type, UPS system suitable for input Power supply voltage of 320 V-460V- TPN (184-265V/Ph), output 230 V +/- 1%, AC with solid state voltage stabilizer for Bypass supply, ACDB and 12.0 hrs. Battery backup (Ni-Cd, 1.2V) and battery capacity shall not be less than 186 KVAh (where KVAH = battery AH x 1.2 V x No. of cells). Charger rating Shall not be Less than 54 KW. | Nos. | 5
2.2 | Dual redundant Rectifier system (AC ro DC) and DCDB as per specification and following rating : (i) 48 V DCDB (2500 W) (ii)24 V DCDB (3500 W) | Nos. | 5
2.3 | All interconnecting cables among UPS, Rectifier, battery stand, ACDB/DCDB etc (50 mtr shall be considered between battery bank and UPS panel, 50 mtr each cable shall be considered between ACDB & DCDB to UPS panel) | Set | 5
2.4 | All inclusive per month rates for maintaining the warehouse/store at site (for supplied material) during the extended period as required (payable if site is not ready even after 6 months of Contractual completion date of Supply, Installation, Testing & commissioning as per terms & condition of contract and as defined in the tender scope of work). | Months | 12
2.5 | 5 years comprehensive AMC for all UPS Supplied. However AMC of these UPS shall start after successful completion of warranty period/ Defect Liability period as per contract. (For detail scope & payment terms refer scope of work & contract document) | LS | 1
3 | ITEM#3- 5KVA UPS SYSTEM
INSTALLATION, TESTING & COMMISSIONING OF UPS SYSTEM IN ASSAM/ ARUNACHAL PRADESH/ TRIPURA/MEGHALAYA STATE/MIZORAM/NAGALAND (REFER SCOPE OF WORK/MR FOR LOCATION OF THE SYSTEM)
Loading/unloading, transportation from warehouse/store (hired by bidder) to site, fabrication, assembly, all mechanical works for installation, erection, commissioning and performance test at site of complete UPS system alongwith bettery sets as mentioned below & as per tender specification, data sheet, PJS enclosed including commissioning spares as required at terminals. The scope also includes submission of first trial/commissioning reports of each location, submission of engineering drawings & documents for approval from IGGL / MECON for UPS System Installation, all other work not indicated here but required for completion of installation & commissioning as per the scope of work in the scope of bidder. Work shall be crried out as per relevant international & national standard, scope of work & specifications, approved drawings & documents.
3.1 | 5KVA, 230 V Single phase, 50 Hz, parallel redundant industrial type, UPS system suitable for input Power supply voltage of 320 V-460V- TPN (184-265V/Ph), output 230 V +/- 1%, AC with solid state voltage stabilizer for Bypass supply, ACDB and 12.0 hrs. Battery backup (Ni-Cd, 1.2V) and battery capacity shall not be less than 93 KVAh (where KVAH = battery AH x 1.2 V x No. of cells). Charger rating Shall not be Less than 27 KW. | Nos. | 13
3.2 | Dual redundant Rectifier system (AC to DC) and DCDB as per specification and following rating : (i) 48 V DCDB (2000 W) (ii) 24 V DCDB (2500W) | Nos. | 13
3.3 | All interconnecting cables among UPS, Rectifier, battery stand, ACDB/DCDB etc (50 mtr shall be considered between battery bank and UPS panel, 50 mtr each cable shall be considered between ACDB & DCDB to UPS panel) | Set | 13
3.4 | All inclusive per month rates for maintaining the warehouse/store at site (for supplied material) during the extended period as required (payable if site is not ready even after 6 months of Contractual completion date of Supply, Installation, Testing & commissioning as per terms & condition of contract and as defined in the tender scope of work). | Months | 12
3.5 | 5 years comprehensive AMC for all UPS Supplied. However AMC of these UPS shall start after successful completion of warranty period/ Defect Liability period as per contract. (For detail scope & payment terms refer scope of work & contract document) | LS | 1
Total price including all costs including GST for SiteWorks
| NOTE: 1.0 The above shall be read in conjunction with notes of MR enclosed with Vol II of II. 2.0 For Statewise quantity breakup please refer scope of work. | [6 empty] | BIDDER'S SIGNATURE:
COMPANY'S NAME:
SEAL:
IGGL
MECON LIMITED

## PS-UPS 2 years spares
UNIT UNPRICE SCHEDULE FOR 2 YEARS O&M SPARES (Addition/Deletion)
UPS SYSTEM FOR PIPELINE SECTIONS (1,2,3,4,5,6,7,8,9,12,13&14) UNDER NORTH EAST GAS GRID PIPELINE PROJET OF M/s IGGL Tender no.: 05/51/23VC/IGGL/071
BIDDER: M/S __________________________
Sl. No. | Description as per MR | Unit | Qty. | Ex-works price (including packing, forwarding, and GST on components and raw materials but excluding Inland Transportation to Delivery Location) including cost of Inspection by Third Party Agency, mandatory spares etc. (wherever applicable) | Inland transportation upto Delivery location and other costs incidental to delivery of goods | GST (CGST&SGST/UTGST or IGST) on the finished goods excluding inland transportation (i.e. on cl. no. 4 ) |  | GST (CGST&SGST/UTGST or IGST) on inland transportation (i.e. on cl. no. 5) |  | Unit FOT site price incl. inland transportaion, GST etc. |  | Total FOT site price incl. inland transportaion, GST etc. |  | Harmonized System Nomenclature (HSN)
[6 empty] | % | Amount | % | Amount | In Figures | In Words | In Figures | In Words
1 | 2.a | 3 | 3a | (4) | (5) | (6) |  | (7) |  | (8)= (4)+(5)+(6)+ (7) |  | (9)= (8) X (3) |  | (10)
1 | IGBT (5 KVA) | Sets | 1
2 | IGBT (10 KVA) | Sets | 1
3 | IGBT (25 KVA) | Sets | 1
4 | Rectifier/ Charger Card* (5 KVA) | Sets | 1
5 | Rectifier/ Charger Card* (10 KVA) | Sets | 1
6 | Rectifier/ Charger Card* (25 KVA) | Sets | 1
7 | Inverter Card* (5 KVA) | Sets | 1
8 | Inverter Card* (10 KVA) | Sets | 1
9 | Inverter Card* (25 KVA) | Sets | 1
10 | Power supply card* (5 KVA) | Sets | 1
11 | Power supply card* (10 KVA) | Sets | 1
12 | Power supply card* (25 KVA) | Sets | 1
13 | DC-DC Converter card* (5 KVA) | Sets | 1
14 | DC-DC Converter card* (10 KVA) | Sets | 1
15 | DC-DC Converter card* (25 KVA) | Sets | 1
16 | Fuse & Indication lights of all ratings** | Sets | 1
17 | Cooling fan | Nos. | 1
18 | MCB's*, Contactors** MCCB's*, Relays** (5 KVA) | Sets | 1
19 | MCB's*, Contactors** MCCB's*, Relays** (10 KVA) | Sets | 1
20 | MCB's*, Contactors** MCCB's*, Relays** (25KVA) | Sets | 1
TOTAL AMOUNT
| Notes: | [8 empty] | BIDDER'S SIGNATURE:
| (1) * One of each rating/type | [8 empty] | COMPANY'S NAME:
| (2) ** 10% of each rating (minimum two number) | [8 empty] | SEAL:
IGGL
MECON LIMITED